## accuracy_summary
task | model | unit | n | MAE | RMSE | R2 | MAPE_% | NMBE_% | acceptance | value | result
Model 1: cooling load | lightgbm | RT | 650 | 18.3842 | 26.2906 | 0.92966 | 3.1542 | 0.64207 | MAPE_% ≤ 5 | 3.1542 | pass
Model 2: weather | lightgbm | °C | 34709 | 0.33815 | 0.58522 | 0.90442 | 1.19 | -0.17625 | MAE ≤ 1 | 0.33815 | pass
Model 3: chiller power | random_forest | kW | 656 | 9.4976 | 15.179 | 0.9493 | 3.5716 | 0.075638 | MAPE_% ≤ 3 | 3.5716 | fail
Model 4: cooling tower | not trained | [7 empty] | MAE ≤ 0.3 |  | no data
Model 5: pump and fan power | not trained | [7 empty] | MAPE_% ≤ 3 |  | no data
Model 6: energy baseline | lightgbm | kW | 656 | 12.1222 | 16.7584 | 0.9382 | 4.4646 | -2.0853 | ¦NMBE¦_% ≤ 5 | 2.0853 | pass

## metrics_all
task | model | split | n | MAE | RMSE | R2 | MAPE_% | CV(RMSE)_% | NMBE_% | ¦NMBE¦_% | within_tol_%
Model 1: cooling load | linear_regression | train | 8256 | 23.9541 | 35.0481 | 0.86241 | 4.5224 | 6.6277 | -9.1764e-15 | 9.1764e-15 | 66.9816
Model 1: cooling load | linear_regression | val | 606 | 24.6241 | 34.6994 | 0.87471 | 4.4062 | 6.2481 | 0.11829 | 0.11829 | 66.5017
Model 1: cooling load | linear_regression | test | 650 | 23.9653 | 33.37 | 0.88668 | 4.2447 | 5.9688 | 0.46602 | 0.46602 | 68.9231
Model 1: cooling load | ridge | train | 8256 | 23.952 | 35.0481 | 0.86241 | 4.522 | 6.6277 | 1.7186e-15 | 1.7186e-15 | 67.0058
Model 1: cooling load | ridge | val | 606 | 24.6181 | 34.6949 | 0.87475 | 4.4051 | 6.2473 | 0.1196 | 0.1196 | 66.5017
Model 1: cooling load | ridge | test | 650 | 23.9609 | 33.3674 | 0.8867 | 4.2439 | 5.9683 | 0.46728 | 0.46728 | 68.9231
Model 1: cooling load | random_forest | train | 8256 | 9.3986 | 15.717 | 0.97233 | 1.7408 | 2.9721 | 0.0068888 | 0.0068888 | 93.7742
Model 1: cooling load | random_forest | val | 606 | 17.8298 | 25.9764 | 0.92979 | 3.0982 | 4.6774 | -0.12402 | 0.12402 | 81.8482
Model 1: cooling load | random_forest | test | 650 | 18.4005 | 26.2549 | 0.92985 | 3.1573 | 4.6961 | 0.10868 | 0.10868 | 80.9231
Model 1: cooling load | mlp | train | 8256 | 14.7303 | 21.9751 | 0.94591 | 2.7327 | 4.1556 | -0.21633 | 0.21633 | 86.4341
Model 1: cooling load | mlp | val | 606 | 20.4268 | 28.5798 | 0.91501 | 3.6239 | 5.1462 | 0.51232 | 0.51232 | 78.2178
Model 1: cooling load | mlp | test | 650 | 22.4122 | 29.7744 | 0.90979 | 3.9928 | 5.3256 | 1.5311 | 1.5311 | 69.0769
Model 1: cooling load | lightgbm | train | 8256 | 12.0007 | 17.7855 | 0.96457 | 2.2473 | 3.3633 | -0.0024669 | 0.0024669 | 90.7703
Model 1: cooling load | lightgbm | val | 606 | 17.3487 | 25.3813 | 0.93297 | 3.0285 | 4.5702 | 0.29297 | 0.29297 | 81.0231
Model 1: cooling load | lightgbm | test | 650 | 18.3842 | 26.2906 | 0.92966 | 3.1542 | 4.7025 | 0.64207 | 0.64207 | 80.6154
Model 1: cooling load | persistence | train | 8256 | 27.2028 | 44.3311 | 0.77988 | 5.0251 | 8.3831 | 0.026264 | 0.026264 | 67.9627
Model 1: cooling load | persistence | val | 606 | 28.5564 | 44.8282 | 0.7909 | 5.0244 | 8.0719 | 0.24276 | 0.24276 | 65.8416
Model 1: cooling load | persistence | test | 650 | 29.1262 | 43.6919 | 0.80574 | 5.0626 | 7.815 | 0.078316 | 0.078316 | 63.6923
Model 1: cooling load | linear_regression | regime_shift | 2651 | 35.518 | 46.677 | 0.50429 | 7.5458 | 9.9952 | 5.7696 | 5.7696 | 43.0026
Model 1: cooling load | ridge | regime_shift | 2651 | 35.4945 | 46.6535 | 0.50479 | 7.5407 | 9.9902 | 5.7635 | 5.7635 | 43.0781
Model 1: cooling load | random_forest | regime_shift | 2651 | 45.7435 | 70.0054 | -0.11502 | 9.4639 | 14.9906 | 8.3662 | 8.3662 | 52.7725
Model 1: cooling load | mlp | regime_shift | 2651 | 61.6067 | 79.7599 | -0.4474 | 13.0972 | 17.0794 | 12.1032 | 12.1032 | 21.7276
Model 1: cooling load | lightgbm | regime_shift | 2651 | 38.7477 | 56.0885 | 0.28424 | 8.0976 | 12.0105 | 6.999 | 6.999 | 52.6594
Model 1: cooling load | persistence | regime_shift | 2651 | 23.1178 | 40.6099 | 0.62478 | 4.5853 | 8.696 | -0.027108 | 0.027108 | 72.1237
Model 2: weather | linear_regression | train | 214876 | 0.37293 | 0.61198 | 0.89719 | 1.3425 | 2.1932 | -2.8483e-14 | 2.8483e-14 | 93.0132
Model 2: weather | linear_regression | val | 33503 | 0.37972 | 0.63203 | 0.90323 | 1.3656 | 2.2632 | -0.0098327 | 0.0098327 | 92.6036
Model 2: weather | linear_regression | test | 34709 | 0.38217 | 0.62108 | 0.89235 | 1.3497 | 2.1936 | -0.16777 | 0.16777 | 92.4486
Model 2: weather | ridge | train | 214876 | 0.37293 | 0.61198 | 0.89719 | 1.3425 | 2.1932 | -9.215e-15 | 9.215e-15 | 93.0136
Model 2: weather | ridge | val | 33503 | 0.37972 | 0.63203 | 0.90323 | 1.3656 | 2.2632 | -0.009833 | 0.009833 | 92.6036
Model 2: weather | ridge | test | 34709 | 0.38217 | 0.62108 | 0.89235 | 1.3497 | 2.1936 | -0.16777 | 0.16777 | 92.4486
Model 2: weather | lightgbm | train | 214876 | 0.31595 | 0.55028 | 0.91687 | 1.1353 | 1.9721 | -2.2534e-05 | 2.2534e-05 | 94.3284
Model 2: weather | lightgbm | val | 33503 | 0.33157 | 0.59321 | 0.91475 | 1.1908 | 2.1242 | -0.019267 | 0.019267 | 93.4275
Model 2: weather | lightgbm | test | 34709 | 0.33815 | 0.58522 | 0.90442 | 1.19 | 2.0669 | -0.17625 | 0.17625 | 93.3447
Model 2: weather | persistence | train | 214876 | 0.47106 | 0.72893 | 0.85413 | 1.6866 | 2.6123 | -0.0040849 | 0.0040849 | 87.4253
Model 2: weather | persistence | val | 33503 | 0.46831 | 0.74334 | 0.86614 | 1.6728 | 2.6618 | 0.0053907 | 0.0053907 | 87.4369
Model 2: weather | persistence | test | 34709 | 0.47006 | 0.73102 | 0.85086 | 1.6541 | 2.5819 | -0.001136 | 0.001136 | 86.963
Model 3: chiller power | linear_regression | train | 9316 | 12.5476 | 18.7312 | 0.90752 | 4.8979 | 7.3346 | 3.517e-14 | 3.517e-14 | 41.5844
Model 3: chiller power | linear_regression | val | 646 | 13.7641 | 19.6752 | 0.92091 | 4.9706 | 7.1647 | -0.88941 | 0.88941 | 38.0805
Model 3: chiller power | linear_regression | test | 656 | 12.7852 | 18.2181 | 0.92697 | 4.569 | 6.5537 | -1.9934 | 1.9934 | 40.3963
Model 3: chiller power | ridge | train | 9316 | 12.5396 | 18.7288 | 0.90755 | 4.8957 | 7.3337 | 2.1541e-13 | 2.1541e-13 | 41.8313
Model 3: chiller power | ridge | val | 646 | 13.728 | 19.6339 | 0.92124 | 4.9599 | 7.1497 | -0.88163 | 0.88163 | 38.5449
Model 3: chiller power | ridge | test | 656 | 12.7507 | 18.1632 | 0.92741 | 4.5635 | 6.534 | -1.9787 | 1.9787 | 40.5488
Model 3: chiller power | random_forest | train | 9316 | 5.2513 | 10.2114 | 0.97252 | 2.0996 | 3.9985 | -0.0038022 | 0.0038022 | 79.4762
Model 3: chiller power | random_forest | val | 646 | 8.9282 | 15.5854 | 0.95037 | 3.3992 | 5.6754 | -0.42859 | 0.42859 | 63.1579
Model 3: chiller power | random_forest | test | 656 | 9.4976 | 15.179 | 0.9493 | 3.5716 | 5.4604 | 0.075638 | 0.075638 | 60.061
Model 3: chiller power | mlp | train | 9316 | 7.8527 | 13.2691 | 0.95359 | 3.1661 | 5.1958 | 0.35874 | 0.35874 | 64.9528
Model 3: chiller power | mlp | val | 646 | 9.1979 | 15.4904 | 0.95098 | 3.5017 | 5.6408 | 0.1144 | 0.1144 | 61.4551
Model 3: chiller power | mlp | test | 656 | 10.015 | 14.9332 | 0.95093 | 3.7335 | 5.372 | 0.70307 | 0.70307 | 55.3354
Model 3: chiller power | lightgbm | train | 9316 | 6.9958 | 11.4045 | 0.96572 | 2.8508 | 4.4657 | 0.0064643 | 0.0064643 | 68.0657
Model 3: chiller power | lightgbm | val | 646 | 9.2162 | 15.5175 | 0.95081 | 3.4631 | 5.6507 | -0.30313 | 0.30313 | 59.7523
Model 3: chiller power | lightgbm | test | 656 | 9.6421 | 14.8368 | 0.95156 | 3.5954 | 5.3373 | 0.14509 | 0.14509 | 58.3841
Model 6: energy baseline | linear_regression | train | 9349 | 18.7395 | 23.6509 | 0.85225 | 7.2712 | 9.2649 | 8.3078e-15 | 8.3078e-15 | 34.8059
Model 6: energy baseline | linear_regression | val | 652 | 20.3231 | 24.6855 | 0.87462 | 7.2657 | 8.9995 | -0.54959 | 0.54959 | 32.0552
Model 6: energy baseline | linear_regression | test | 656 | 19.4095 | 23.0023 | 0.88357 | 6.796 | 8.2747 | -1.6217 | 1.6217 | 27.5915
Model 6: energy baseline | ridge | train | 9349 | 18.7469 | 23.651 | 0.85225 | 7.2743 | 9.265 | -8.6927e-14 | 8.6927e-14 | 34.6668
Model 6: energy baseline | ridge | val | 652 | 20.3329 | 24.691 | 0.87457 | 7.2679 | 9.0015 | -0.5541 | 0.5541 | 32.0552
Model 6: energy baseline | ridge | test | 656 | 19.4194 | 23.0139 | 0.88345 | 6.798 | 8.2789 | -1.6253 | 1.6253 | 27.5915
Model 6: energy baseline | random_forest | train | 9349 | 7.4903 | 12.4354 | 0.95915 | 2.9644 | 4.8714 | 0.02418 | 0.02418 | 83.7844
Model 6: energy baseline | random_forest | val | 652 | 13.0237 | 18.7819 | 0.92742 | 4.8779 | 6.8472 | -1.1407 | 1.1407 | 65.184
Model 6: energy baseline | random_forest | test | 656 | 11.9423 | 16.9258 | 0.93696 | 4.3819 | 6.0888 | -2.0197 | 2.0197 | 64.939
Model 6: energy baseline | mlp | train | 9349 | 10.757 | 15.9073 | 0.93316 | 4.2521 | 6.2315 | -0.16031 | 0.16031 | 69.1839
Model 6: energy baseline | mlp | val | 652 | 13.7276 | 19.3468 | 0.92299 | 5.1096 | 7.0532 | -0.73558 | 0.73558 | 60.8896
Model 6: energy baseline | mlp | test | 656 | 12.8783 | 17.3649 | 0.93365 | 4.724 | 6.2468 | -1.7987 | 1.7987 | 60.3659
Model 6: energy baseline | lightgbm | train | 9349 | 9.7005 | 14.5001 | 0.94446 | 3.8799 | 5.6802 | 0.0017076 | 0.0017076 | 74.4251
Model 6: energy baseline | lightgbm | val | 652 | 13.2012 | 18.7001 | 0.92805 | 4.9277 | 6.8174 | -1.2567 | 1.2567 | 65.3374
Model 6: energy baseline | lightgbm | test | 656 | 12.1222 | 16.7584 | 0.9382 | 4.4646 | 6.0286 | -2.0853 | 2.0853 | 64.939

## acceptance_rules
task | metric | limit | meaning
Model 1: cooling load | MAPE_% | 5 | mean absolute % error of the next-hour load ≤ 5 %
Model 2: weather | MAE | 1 | mean absolute error of the next-hour dry-bulb ≤ 1 °C
Model 3: chiller power | MAPE_% | 3 | mean absolute % error of chiller kW ≤ 3 %
Model 4: cooling tower | MAE | 0.3 | mean absolute error of tower leaving water ≤ 0.3 °C
Model 5: pump and fan power | MAPE_% | 3 | mean absolute % error of pump / fan kW ≤ 3 %
Model 6: energy baseline | ¦NMBE¦_% | 5 | total energy over the test period within ± 5 %

## model4_data_availability
measurement | CSIT tags | max samples | class
tower leaving water temperature | CT1.SupTemp, CT2.SupTemp, CT3.SupTemp | 66 | snapshot
tower return (entering) temperature | CT1.RetTemp, CT2.RetTemp, CT3.RetTemp | 66 | snapshot
tower fan speed feedback | CT1.A_Fan_ECFbk, CT1.B_Fan_ECFbk, CT1.C_Fan_ECFbk, CT2.A_Fan_ECFbk, CT2.B_Fan_ECFbk, CT2.C_Fan_ECFbk, CT3.A_Fan_ECFbk, CT3.B_Fan_ECFbk, CT3.C_Fan_ECFbk | 66 | snapshot
condenser water flow | FLOTECH.CH1_CW_Flow, FLOTECH.CH2_CW_Flow, FLOTECH.CH3_CW_Flow, CH1.CW_Flow, CH2.CW_Flow | 66 | snapshot
outdoor wet-bulb | OA_WetBulbT.WetBulb_Temp | 66 | snapshot

## model5_data_availability
measurement | CSIT tags | max samples | class
CHW pump power (per pump) | CHWP1.kW, CHWP2.kW, CHWP3.kW | 5870 | trend
CW pump power (per pump) | CWP1.kWatt, CWP2.kWatt, CWP3.kWatt | 25402 | trend
tower fan power (per cell) | CT1.kWatt, CT2.kWatt, CT3.kWatt | 9267 | trend
pump / fan power (aggregate) | CHWP.PMKWtotal, CWP.PMKWtotal, CT.PMKWtotal | 4686 | trend
pump VSD speed feedback | CWP1.VSDFdk, CWP1.VSDFbk, CWP2.VSDFbk, CWP3.VSDFbk, CHWP1.VSDFdk, CHWP2.VSDFdk, CHWP3.VSDFdk | 66 | empty, snapshot
tower fan speed feedback | CT1.A_Fan_ECFbk, CT1.B_Fan_ECFbk, CT1.C_Fan_ECFbk, CT2.A_Fan_ECFbk, CT2.B_Fan_ECFbk, CT2.C_Fan_ECFbk, CT3.A_Fan_ECFbk, CT3.B_Fan_ECFbk, CT3.C_Fan_ECFbk | 66 | snapshot
chilled water flow | FLOTECH.CH1_CHW_Flow, FLOTECH.CH2_CHW_Flow, FLOTECH.CH3_CHW_Flow, CH1.CHW_Flow, CH2.CHW_Flow | 66 | snapshot
condenser water flow | FLOTECH.CH1_CW_Flow, FLOTECH.CH2_CW_Flow, FLOTECH.CH3_CW_Flow, CH1.CW_Flow, CH2.CW_Flow | 66 | snapshot

## split_summary
level_0 | split | rows | rows_with_target | start | end | days | target_mean
uwcsea | train | 9838 | 9388 | 2019-08-18 | 2020-03-09 22:30 | 205 | 531.1607
uwcsea | val | 670 | 658 | 2020-03-10 | 2020-03-23 22:30 | 14 | 556.6567
uwcsea | test | 672 | 668 | 2020-03-24 | 2020-04-06 23:30 | 14 | 557.7399
uwcsea | regime_shift | 2667 | 2665 | 2020-04-07 | 2020-06-01 13:00 | 56 | 466.7094
csit | train | 2026 | 112 | 2026-09-01 19:15 | 2026-10-13 22:45 | 23 | 42.7131
csit | val | 92 | 92 | 2026-10-14 | 2026-10-14 22:45 | 1 | 92.9499
csit | test | 87 | 87 | 2026-10-15 | 2026-10-15 21:30 | 1 | 97.3011
nea | train | 235312 | 225691 | 2016-04-15 19:00 | 2022-12-31 22:45 | 2452 | 27.898
nea | val | 35036 | 33991 | 2023-01-01 | 2023-12-31 22:45 | 365 | 27.9238
nea | test | 35136 | 34964 | 2024-01-01 | 2024-12-31 23:45 | 366 | 28.3126

## feature_importance
task | feature | gain_%
Model 1 | hour_cos | 52.8318
Model 1 | load_rt | 28.1781
Model 1 | is_workday | 6.0288
Model 1 | hour_sin | 2.6884
Model 1 | load_rt_lag_30min | 2.2053
Model 1 | load_rt_rollmean_2h | 1.2614
Model 1 | load_rt_rollmean_1D | 1.1369
Model 1 | doy_cos | 0.78408
Model 1 | load_rt_lag_7D | 0.70828
Model 1 | chw_flow_lps | 0.64925
Model 1 | load_rt_lag_2h | 0.50883
Model 1 | dow_sin | 0.4768
Model 1 | cw_temp_c | 0.45031
Model 1 | wetbulb_c | 0.32653
Model 1 | doy_sin | 0.29657
Model 2 | drybulb_c | 68.222
Model 2 | drybulb_c_lag_15min | 12.4964
Model 2 | drybulb_c_rollmax_1h | 8.5961
Model 2 | drybulb_diff_15min | 3.3103
Model 2 | drybulb_c_rollmean_1h | 2.7548
Model 2 | hour_cos | 2.296
Model 2 | hour_sin | 0.79968
Model 2 | doy_cos | 0.27784
Model 2 | drybulb_c_rollstd_1h | 0.24637
Model 2 | drybulb_c_lag_3h | 0.17929
Model 2 | doy_sin | 0.17582
Model 2 | drybulb_c_rollmax_3h | 0.15775
Model 2 | drybulb_c_lag_1D | 0.12158
Model 2 | drybulb_c_lag_2h | 0.097197
Model 2 | drybulb_c_rollstd_3h | 0.078521